## IBS DPA 500 Master
ID-CARD DPA 500
FRAME 500 kVA
Customer: |  | Digiplex Fet (DFAS) |  |  |  |  | Address: |  |  |  | Heiaveien
Date of service: |  | 2020-05-11 |  |  |  |  | Customer contact: |  |  |  | Dag Brækken
UPS ID (Trinn/Side): |  | A1-2A UPS1 |  |  |  |  | Service contract nr: |  |  |  | ABBUPS001115
UPS system |  | Coneptpower DPA500 |  |  |  |  | Active |  | Passive |  | System int. nr. |  | Comm. Date
Frame serial Nr.: |  | 5U 0109 |  |  |  | P 01: | DXM000413 |  | P5M0403 |  | 1 |  | 2015-02-18
Frame No. (Hir): |  | 1 (Master) |  |  |  | P 02: | DXM000411 |  | P5M0404 |  | 2 |  | 2015-02-18
Commiss. Date: |  | 2015-02-18 |  |  |  | P 03: | DXM000398 |  | P5M0391 |  | 3 |  | 2015-02-18
UPS Segment: |  | Datacenter |  |  |  | P 04 | DXM000396 |  | P5M0389 |  | 4 |  | 2015-02-18
[6 empty] | P 05: | DXM000395 |  | P5M0388 |  | 5 |  | 2015-02-18
GENERAL:
BATTERY | Backup time / load |  | 4 min / 100 kW |  |  | SYSTEM |  | SYSTEM CONFIGUR. |  |  | Parallell
| Amount of blocks |  | 40 |  |  |  |  | NR. PARALL. FRAMES |  |  | 3
| Set float voltage |  | 547 |  |  |  |  | MODULE POWER |  |  | 100kKVA
| Set cut off voltage |  | 393 |  |  |  |  | NOMINAL VOLTAGE |  |  | 400V
| Charge current limitation |  | Yes |  |  |  |  | FREQUENCY |  |  | 50Hz
| Fast charge |  | Auto |  |  |  |  | SYNCH. WINDOW |  |  | Yes
| Common / modular |  | Modular |  |  |  |  | SYNCH. WINDOW |  |  | Online
| Manufacturer |  | GNB Exide |  |  |  |  | SYNCH. WINDOW
| Type |  | M. XL12V70 |  |  |  |  | SYNCH. WINDOW
| Nominal capcity |  | 70 Ah
SET-UP INFO | ACTIVE MODULE SERIAL NR |  |  | DXM000413 |  | DXM000411 |  | DXM000398 |  | DXM000396 |  | DXM000395
| DATE(MONTH) OF MANUFACT. |  |  | 11/12/14 |  | 11/12/14 |  | 05/12/14 |  | 05/12/14 |  | 05/12/14
| EPROM VER |  |  | 1.55 448D |  | 1.55 448D |  | 1.55 448D |  | 1.55 448D |  | 1.55 448D
| HARDWARE VERSION |  |  | 00000080 |  | 00000080 |  | 00000080 |  | 00000080 |  | 00000080
| DYN. PASSWORD |  |  | NO |  | NO |  | NO |  | NO |  | NO
REMARKS | All fans and rear connections inspected and OK. Downloaded system event log. Defect batteries detected (Ref comments in Batt. Measurement) Fan and capacitor replacement recommended at nex service (Spring 2020)
ABB Service Engineers (On-Site): |  |  |  | 1. | ABB - Svein Andersen
|  |  |  | 2. | ABB - Christopher Kooij
Customer Representative (On-Site): |  |  |  | 3. | Digiplex Fet - Dag Brækken
Common battery
Modular battery
SNMP Standard
SNMP Modbus
General alarm when redundancy lost
General alarm when first alarm
Output breaker pos. connected
External bypass pos. connected
Single Feed Input
Dual Feed Input
Other external connection, specity in "remarks"
Internal maint. bypass
External maint. bypass

## REV DPA 500 Master
Revision DPA 500
FRAME 500 kVA
Kunde: |  |  | Digiplex Fet (DFAS) |  |  |  |  | Address: |  |  |  | Heiaveien
Date of service: |  |  | 2020-05-11 |  |  |  |  | Customer contact: |  |  |  | Dag Brækken
UPS ID (Trinn/Side): |  |  | A1-2A UPS1 |  |  |  |  | Contract Nr: |  |  |  | ABBUPS001115
Frame No: |  |  | Frame 1 |  |  |  | Mod: |  | Active: |  |  |  | Passive:
Frame Serial Nr: |  |  | 5U 0109 |  |  |  | P 01: |  | DXM000413 |  |  |  | P5M0403
Frame Hir: |  |  | 1 (Master) |  |  |  | P 02: |  | DXM000411 |  |  |  | P5M0404
[7 empty] | P 03: |  | DXM000398 |  |  |  | P5M0391
[7 empty] | P 04: |  | DXM000396 |  |  |  | P5M0389
[7 empty] | P 05: |  | DXM000395 |  |  |  | P5M0388
System display readings: |  |  |  |  | P 01: | DXM000413 |  |  | P 02: | DXM000411 |  |  | P 03: | DXM000398
Battery float voltage |  |  |  |  | 545 |  |  |  | 545 |  |  |  | 545
[5 empty] | L1 | L2 | L3 |  | L1 | L2 | L3 |  | L1 | L2 | L3
Rectifier voltage |  |  |  |  | 237 | 239 | 240 | V | 236 | 237 | 238 | V | 236 | 237 | 238 | V
Bypass voltage |  |  |  |  | 237 | 239 | 240 | V | 236 | 237 | 238 | V | 236 | 237 | 238 | V
Inverter output voltage |  |  |  |  | 230 | 230 | 230 | V | 230 | 230 | 230 | V | 230 | 230 | 230 | V
Load current |  |  |  |  | 19.3 | 28.5 | 18.2 | A | 18.3 | 28.8 | 17.4 | A | 18.8 | 28.2 | 16.9 | A
Load active power |  |  |  |  | 3.9 | 6.2 | 3.9 | kW | 3.9 | 6.2 | 3.8 | kW | 4.0 | 6.2 | 3.8 | kW
Load reactive power |  |  |  |  | -1.7 | -1.6 | -1.8 | kVar | -1.6 | -1.6 | - 1.2 | kVar | -1.2 | -1.7 | -1.0 | kVar
Load apparent power |  |  |  |  | 4.2 | 6.2 | 4.1 | kVA | 4.1 | 6.5 | 4.0 | kVA | 4.3 | 6.4 | 3.9 | kVA
Load of nominal |  |  |  |  | 12 | 19 | 12 | % | 12 | 19 | 12 | % | 12 | 19 | 12 | %
[5 empty] | P 04 | DXM000396 |  |  | P 05: | DXM000395
Battery float voltage |  |  |  |  | 545 |  |  |  | 545
[5 empty] | L1 | L2 | L3 |  | L1 | L2 | L3
Rectifier voltage |  |  |  |  | 236 | 237 | 238 | V | 236 | 237 | 238 | V
Bypass voltage |  |  |  |  | 236 | 237 | 238 | V | 236 | 237 | 238 | V
Inverter output voltage |  |  |  |  | 230 | 230 | 230 | V | 230 | 230 | 230 | V
Load current |  |  |  |  | 18.8 | 28.8 | 18.9 | A | 18.8 | 32.2 | 18.8 | A
Load active power |  |  |  |  | 3.8 | 6.3 | 3.9 | kW | 4 | 6.5 | 4.1 | kW
Load reactive power |  |  |  |  | -1.8 | -2.1 | -1.5 | kVar | -1.6 | -2.2 | -1.6 | kVar
Load apparent power |  |  |  |  | 4.2 | 6.6 | 4.2 | kVA | 4.4 | 6.9 | 4.4 | kVA
Load of nominal |  |  |  |  | 12 | 20 | 12 | % | 12 | 20 | 12 | %
Test & Control Checklist:
See separate page.
[5 empty] | °C | 20
[13 empty] | In use since: |  | Commissioning
[13 empty] | In use since: |  | Commissioning
[13 empty] | In use since: |  | Commissioning
Measurements:
Rectifier input: | [9 empty] | Load:
Phase L1-N: |  | 237 | V | - | A |  |  |  |  | Phase L1-N: |  | 230 | V | - | A
Phase L2-N: |  | 239 | V | - | A |  |  |  |  | Phase L2-N: |  | 230 | V | - | A
Phase L3-N: |  | 240 | V | - | A |  |  |  |  | Phase L3-N: |  | 230 | V | - | A
| COMPLETED BY (Company / Person): | [5 empty] | ABB AS - Svein Andersen
| DATE: | [5 empty] | 2020-05-11
Tested INVERTER - BYPASS
Verified fan function:
Customer logbook update
Tested with diesel-generator
Battery test:
Max. charge current verified
Event Log File check (download)
Visual inspection
Cleaning
UPS room temperature:
Operating modes test
Remote alarms and controls test
SNMP Adapter
Check paramater settings
Battery charger function verified
Batt. Test active:
Yes
No:
External bypass:
Yes
No
Yes
No
Modules ON-OFF-ON
Control AC caps.:
Control DC caps.:

## Battery Measurement 1
Battery Test Records
Customer: | Digiplex Fet (DFAS) |  |  | Frame serial Nr.: |  | 5U 0109 |  |  | Address: |  | Heiaveien
Date of service: | 2020-05-11 |  |  | Frame No. (Hir): |  | 1 (Master) |  |  | Customer contact: |  | Dag Brækken
UPS ID (Trinn/Side): | A1-2A UPS1 | [7 empty] | Contract Nr: |  | ABBUPS001115
String Values during Battery test: |  | MONITORED BY CELLWATCH
Mod: | S/N_ Branch For: |  | No Load V: | Load Applied.(W) |  | 1` Value (V) | 3` Value (V) | 7` Value (V) | 10` Value (V) | 20` Value (V) |  | 30` Value (V)
P 01: | DXM000413 |  | 545 | 15000 |  | 496 | 487 | 489 | 488 | 486 |  | 482
P 02: | DXM000411 |  | 545 | 15000 |  | 496 | 489 | 492 | 489 | 486 |  | 482
P 03: | DXM000398 |  | 545 | 15000 |  | 496 | 488 | 489 | 489 | 486 |  | 482
P 04: | DXM000396 |  | 545 | 15000 |  | 498 | 488 | 489 | 488 | 485 |  | 479
P 05: | DXM000395 |  | 545 | 15000 |  | 501 | 488 | 489 | 489 | 486 |  | 482
Test & Control Checklist:
[5 empty] | °C | 20
[5 empty] | Name: | -
REMARKS / CORRECTIONS: |  | Aut. Battery test performed 30min - Result: 1 x Battery to be replaced:
String P1 / Block 30 defect, voltage drop (9Vdc)
Room Conditions
Thermography
Termination and identification
DC Protection functionallity and Alarm

## IBS DPA 500 Middle
ID-CARD DPA 500
FRAME 500 kVA
Customer: |  | Digiplex Fet (DFAS) |  |  |  |  | Address: |  |  |  | Heiaveien
Date of service: |  | 2020-05-11 |  |  |  |  | Customer contact: |  |  |  | Dag Brækken
UPS ID (Trinn/Side): |  | A1-2A UPS2 |  |  |  |  | Service contract nr: |  |  |  | ABBUPS001115
UPS system |  | Coneptpower DPA500 |  |  |  |  | Active |  | Passive |  | System int. nr. |  | Comm. Date
Frame serial Nr.: |  | 5U 0110 |  |  |  | P 06: | DXM000409 |  | P5M0402 |  | 1 |  | 2015-02-18
Frame No. (Hir): |  | 2 (Slave) |  |  |  | P 07: | DXM000419 |  | P5M0407 |  | 2 |  | 2015-02-18
Commiss. Date: |  | 2015-02-18 |  |  |  | P 08: | DXM000400 |  | P5M0393 |  | 3 |  | 2015-02-18
UPS Segment: |  | Datacenter |  |  |  | P 09: | DXM000399 |  | P5M0392 |  | 4 |  | 2015-02-18
[6 empty] | P 10: | DXM000410 |  | P5M0375 |  | 5 |  | 2015-02-18
GENERAL:
BATTERY | Backup time / load |  | 4 min / 100 kW |  |  | SYSTEM |  | SYSTEM CONFIGUR. |  |  | Parallell
| Amount of blocks |  | 40 |  |  |  |  | NR. PARALL. FRAMES |  |  | 3
| Set float voltage |  | 547 |  |  |  |  | MODULE POWER |  |  | 100kKVA
| Set cut off voltage |  | 393 |  |  |  |  | NOMINAL VOLTAGE |  |  | 400V
| Charge current limitation |  | Yes |  |  |  |  | FREQUENCY |  |  | 50Hz
| Fast charge |  | Auto |  |  |  |  | SYNCH. WINDOW |  |  | Yes
| Common / modular |  | Modular |  |  |  |  | OPER. MODE |  |  | Online
| Manufacturer |  | GNB Exide
| Type |  | M. XL12V70
| Nominal capcity |  | 70 Ah
SET-UP INFO | ACTIVE MODULE SERIAL NR |  |  | DXM000409 |  | DXM000419 |  | DXM000400 |  | DXM000399 |  | DXM000410
| DATE(MONTH) OF MANUFACT. |  |  | 11/12/14 |  | 09/12/14 |  | 10/12/14 |  | 10/12/14 |  | 11/12/14
| EPROM VER |  |  | 1.55 448D |  | 1.55 448D |  | 1.55 448D |  | 1.55 448D |  | 1.55 448D
| HARDWARE VERSION |  |  | 00000080 |  | 00000080 |  | 00000080 |  | 00000080 |  | 00000080
| DYN. PASSWORD |  |  | NO |  | NO |  | NO |  | NO |  | NO
REMARKS | All fans and rear connections inspected and OK. Downloaded system event log. Battery tested OK. Fan and capacitor replacement recommended on next service.
ABB Service Engineers (On-Site): |  |  |  | 1. | ABB - Svein Andersen
|  |  |  | 2. | ABB - Christopher Kooij
Customer Representative (On-Site): |  |  |  | 3. | Digiplex Fet - Dag Brækken
Common battery
Modular battery
SNMP Standard
SNMP Modbus
General alarm when redundancy lost
General alarm when first alarm
Output breaker pos. connected
External bypass pos. connected
Single Feed Input
Dual Feed Input
Other external connection, specity in "remarks"
Internal maint. bypass
External maint. bypass

## REV DPA 500 Middle
Revision DPA 500
FRAME 500 kVA
Kunde: |  |  | Digiplex Fet (DFAS) |  |  |  |  | Address: |  |  |  | Heiaveien
Date of service: |  |  | 2020-05-11 |  |  |  |  | Customer contact: |  |  |  | Dag Brækken
UPS ID (Trinn/Side): |  |  | A1-2A UPS2 |  |  |  |  | Contract Nr: |  |  |  | ABBUPS001115
Frame No: |  |  | Frame 2 |  |  |  | Mod: |  | Active: |  |  |  | Passive:
Frame Serial Nr: |  |  | 5U 0110 |  |  |  | P 06: |  | DXM000409 |  |  |  | P5M0402
Frame Hir: |  |  | 2 (Slave) |  |  |  | P 07: |  | DXM000419 |  |  |  | P5M0407
[7 empty] | P 08: |  | DXM000400 |  |  |  | P5M0393
[7 empty] | P 09: |  | DXM000399 |  |  |  | P5M0392
[7 empty] | P 10: |  | DXM000410 |  |  |  | P5M0375
System display readings: |  |  |  |  | P 06: | DXM000409 |  |  | P 07: | DXM000419 |  |  | P 08: | DXM000400
Battery float voltage |  |  |  |  | 545 |  |  |  | 545 |  |  |  | 545
[5 empty] | L1 | L2 | L3 |  | L1 | L2 | L3 |  | L1 | L2 | L3
Rectifier voltage |  |  |  |  | 237 | 238 | 239 | V | 237 | 238 | 239 | V | 237 | 238 | 239 | V
Bypass voltage |  |  |  |  | 237 | 238 | 239 | V | 237 | 238 | 239 | V | 237 | 238 | 239 | V
Inverter output voltage |  |  |  |  | 230 | 230 | 230 | V | 230 | 230 | 230 | V | 230 | 230 | 230 | V
Load current |  |  |  |  | 18.2 | 28.3 | 18.1 | A | 18.9 | 28.3 | 18.2 | A | 19.1 | 28.1 | 17 | A
Load active power |  |  |  |  | 3.8 | 6.1 | 3.8 | kW | 3.9 | 6.2 | 3.9 | kW | 4.1 | 6.4 | 3.8 | kW
Load reactive power |  |  |  |  | -1.5 | -1.2 | -1.4 | kVar | -1.6 | -1.6 | -1.5 | kVar | -1.8 | -1.8 | -1.1 | kVar
Load apparent power |  |  |  |  | 4.2 | 6.5 | 4.1 | kVA | 4.4 | 6.6 | 4.1 | kVA | 4.5 | 6.4 | 3.8 | kVA
Load of nominal |  |  |  |  | 13 | 19 | 12 | % | 13 | 19 | 12 | % | 13 | 18 | 12 | %
[5 empty] | P 09: | DXM000399 |  |  | P 10: | DXM000410
Battery float voltage |  |  |  |  | 545 |  |  |  | 545
[5 empty] | L1 | L2 | L3 |  | L1 | L2 | L3
Rectifier voltage |  |  |  |  | 237 | 238 | 239 | V | 237 | 238 | 239 | V
Bypass voltage |  |  |  |  | 237 | 238 | 239 | V | 237 | 238 | 239 | V
Inverter output voltage |  |  |  |  | 230 | 230 | 230 | V | 230 | 230 | 230 | V
Load current |  |  |  |  | 18 | 28.1 | 17.9 | A | 19.7 | 29 | 19 | A
Load active power |  |  |  |  | 3.9 | 6.2 | 3.8 | kW | 4 | 6.4 | 3.9 | kW
Load reactive power |  |  |  |  | -1.5 | -1.8 | -1.5 | kVar | -1.8 | -1.9 | -1.6 | kVar
Load apparent power |  |  |  |  | 4.2 | 6.4 | 4.1 | kVA | 4.6 | 6.7 | 4.3 | kVA
Load of nominal |  |  |  |  | 12 | 18 | 12 | % | 13 | 19 | 13 | %
Test & Control Checklist:
See separate page.
[5 empty] | °C | 20
[13 empty] | In use since: |  | Commissioning
[13 empty] | In use since: |  | Commissioning
[13 empty] | In use since: |  | Commissioning
Measurements:
Rectifier input: | [9 empty] | Load:
Phase L1-N: |  | 239 | V | - | A |  |  |  |  | Phase L1-N: |  | 230.1 | V | - | A
Phase L2-N: |  | 240 | V | - | A |  |  |  |  | Phase L2-N: |  | 229.8 | V | - | A
Phase L3-N: |  | 241 | V | - | A |  |  |  |  | Phase L3-N: |  | 229.6 | V | - | A
| COMPLETED BY (Company / Person): | [5 empty] | ABB AS - Svein Andersen
| DATE: | [5 empty] | 2020-05-11
Tested INVERTER - BYPASS
Verified fan function:
Customer logbook update
Tested with diesel-generator
Battery test:
Max. charge current verified
Event Log File check (download)
Visual inspection
Cleaning
UPS room temperature:
Operating modes test
Remote alarms and controls test
SNMP Adapter
Check paramater settings
Battery charger function verified
Batt. Test active:
Yes
No:
External bypass:
Yes
No
Yes
No
Modules ON-OFF-ON
Control AC caps.:
Control DC caps.:

## Battery Measurement 2
Battery Test Records
Customer: | Digiplex Fet (DFAS) |  |  | Frame serial Nr.: |  | 5U 0110 |  |  | Address: |  | Heiaveien
Date of service: | 2020-05-12 |  |  | Frame No. (Hir): |  | 2 (Slave) |  |  | Customer contact: |  | Dag Brækken
UPS ID (Trinn/Side): | A1-2A UPS2 | [7 empty] | Contract Nr: |  | ABBUPS001115
String Values during Battery test: |  | MONITORED BY CELLWATCH
Mod: | S/N_ Branch For: |  | No Load V: | Load Applied.(W) |  | 1` Value (V) | 3` Value (V) | 7` Value (V) | 10` Value (V) | 20` Value (V) |  | 30` Value (V)
P 06: | DXM000409 |  | 545 | 15000 |  | 487 | 489 | 491 | 491 | 488 |  | 484
P 07: | DXM000419 |  | 545 | 15000 |  | 486 | 488 | 489 | 489 | 485 |  | 480
P 08: | DXM000400 |  | 545 | 15000 |  | 486 | 488 | 489 | 488 | 483 |  | 477
P 09: | DXM000399 |  | 545 | 15000 |  | 483 | 484 | 485 | 485 | 482 |  | 478
P 10: | DXM000410 |  | 545 | 15000 |  | 486 | 488 | 489 | 488 | 484 |  | 480
Test & Control Checklist:
[5 empty] | °C | 20
[5 empty] | Name: | -
REMARKS / CORRECTIONS: |  | Aut. Battery test performed 30min - Result: 1 x Battery to be replaced:
String P9 / Block 2 defect, voltage drop (9Vdc)
Room Conditions
Thermography
Termination and identification
DC Protection functionallity and Alarm

## IBS DPA 500 End Frame
ID-CARD DPA 500
FRAME 500 kVA
Customer: |  | Digiplex Fet (DFAS) |  |  |  |  | Address: |  |  |  | Heiaveien
Date of service: |  | 2020-05-11 |  |  |  |  | Customer contact: |  |  |  | Dag Brækken
UPS ID (Trinn/Side): |  | A1-2A UPS3 |  |  |  |  | Service contract nr: |  |  |  | ABBUPS001115
UPS system |  | Coneptpower DPA500 |  |  |  |  | Active |  | Passive |  | System int. nr. |  | Comm. Date
Frame serial Nr.: |  | 5U 0111 |  |  |  | P 11: | DXM000424 |  | P5M0266 |  | 1 |  | 2015-02-18
Frame No. (Hir): |  | 3 (Slave) |  |  |  | P 12: | DXM000420 |  | P5M0413 |  | 2 |  | 2015-02-18
Commiss. Date: |  | 2015-02-18 |  |  |  | P 13: | DXM000415 |  | P5M0406 |  | 3 |  | 2015-02-18
UPS Segment: |  | Datacenter |  |  |  | P 14: | DXM000421 |  | P5M0405 |  | 4 |  | 2015-02-18
[6 empty] | P 15: | DXM000423 |  | P5M0302 |  | 5 |  | 2015-02-18
GENERAL:
BATTERY | Backup time / load |  | 4 min / 100 kW |  |  | SYSTEM |  | SYSTEM CONFIGUR. |  |  | Parallell
| Amount of blocks |  | 40 |  |  |  |  | NR. PARALL. FRAMES |  |  | 3
| Set float voltage |  | 547 |  |  |  |  | MODULE POWER |  |  | 100kKVA
| Set cut off voltage |  | 393 |  |  |  |  | NOMINAL VOLTAGE |  |  | 400V
| Charge current limitation |  | Yes |  |  |  |  | FREQUENCY |  |  | 50Hz
| Fast charge |  | Auto |  |  |  |  | SYNCH. WINDOW |  |  | Yes
| Common / modular |  | Modular |  |  |  |  | OPER. MODE |  |  | Online
| Manufacturer |  | GNB Exide
| Type |  | M. XL12V70
| Nominal capcity |  | 70 Ah
SET-UP INFO | ACTIVE MODULE SERIAL NR |  |  | DXM000424 |  | DXM000420 |  | DXM000415 |  | DXM000421 |  | DXM000423
| DATE(MONTH) OF MANUFACT. |  |  | 15/12/14 |  | 12/12/14 |  | 11/12/14 |  | 12/12/14 |  | 12/12/14
| EPROM VER |  |  | 1,55 448D |  | 1,55 448D |  | 1,55 448D |  | 1,55 448D |  | 1,55 448D
| HARDWARE VERSION |  |  | 00000080 |  | 00000080 |  | 00000080 |  | 00000080 |  | 00000080
| DYN. PASSWORD |  |  | NO |  | NO |  | NO |  | NO |  | NO
REMARKS | All fans and rear connections inspected and OK. Downloaded system event log. Defect batteries detected (Ref comments in Batt. Measurement) Fan and capacitor replacement recommended at next service
ABB Service Engineers (On-Site): |  |  |  | 1. | ABB - Svein Andersen
|  |  |  | 2. | ABB - Christopher Kooij
Customer Representative (On-Site): |  |  |  | 3. | Digiplex Fet - Dag Brækken
Common battery
Modular battery
SNMP Standard
SNMP Modbus
General alarm when redundancy lost
General alarm when first alarm
Output breaker pos. connected
External bypass pos. connected
Single Feed Input
Dual Feed Input
Other external connection, specity in "remarks"
Internal maint. bypass
External maint. bypass

## REV DPA 500 End Frame
Revision DPA 500
FRAME 500 kVA
Kunde: |  |  | Digiplex Fet (DFAS) |  |  |  |  | Address: |  |  |  | Heiaveien
Date of service: |  |  | 2020-05-11 |  |  |  |  | Customer contact: |  |  |  | Dag Brækken
UPS ID (Trinn/Side): |  |  | A1-2A UPS3 |  |  |  |  | Contract Nr: |  |  |  | ABBUPS001115
Frame No: |  |  | Frame 3 |  |  |  | Mod: |  | Active: |  |  |  | Passive:
Frame Serial Nr: |  |  | 5U 0111 |  |  |  | P 11: |  | DXM000424 |  |  |  | P5M0266
Frame Hir: |  |  | 3 (Slave) |  |  |  | P 12: |  | DXM000420 |  |  |  | P5M0413
[7 empty] | P 13: |  | DXM000415 |  |  |  | P5M0406
[7 empty] | P 14: |  | DXM000421 |  |  |  | P5M0405
[7 empty] | P 15: |  | DXM000423 |  |  |  | P5M0302
System display readings: |  |  |  |  | P 11: | DXM000424 |  |  | P 12: | DXM000420 |  |  | P 13: | DXM000415
Battery float voltage |  |  |  |  | 545 |  |  |  | 545 |  |  |  | 545
[5 empty] | L1 | L2 | L3 |  | L1 | L2 | L3 |  | L1 | L2 | L3
Rectifier voltage |  |  |  |  | 237 | 238 | 239 | V | 237 | 238 | 239 | V | 237 | 238 | 239 | V
Bypass voltage |  |  |  |  | 237 | 238 | 239 | V | 237 | 238 | 239 | V | 237 | 238 | 239 | V
Inverter output voltage |  |  |  |  | 230 | 230 | 230 | V | 230 | 230 | 230 | V | 230 | 230 | 230 | V
Load current |  |  |  |  | 19.2 | 28.7 | 18.9 | A | 18.8 | 27.2 | 1.8 | A | 18.9 | 27 | 18.8 | A
Load active power |  |  |  |  | 4 | 6.3 | 4 | kW | 4.1 | 6.1 | 4 | kW | 4 | 6.1 | 3.9 | kW
Load reactive power |  |  |  |  | -1.8 | -1.9 | -1.2 | kVar | -1.5 | -1.6 | -1.3 | kVar | -1.5 | -1.6 | -1.4 | kVar
Load apparent power |  |  |  |  | 4.5 | 6.8 | 4.4 | kVA | 4.2 | 6.2 | 4.1 | kVA | 4.3 | 6.3 | 3.9 | kVA
Load of nominal |  |  |  |  | 13 | 20 | 12 | % | 12 | 19 | 12 | % | 13 | 18 | 11 | %
[5 empty] | P 14: | DXM000421 |  |  | P 15: | DXM000423
Battery float voltage |  |  |  |  | 545 |  |  |  | 545
[5 empty] | L1 | L2 | L3 |  | L1 | L2 | L3
Rectifier voltage |  |  |  |  | 237 | 238 | 239 | V | 237 | 238 | 239 | V
Bypass voltage |  |  |  |  | 237 | 238 | 239 | V | 237 | 238 | 239 | V
Inverter output voltage |  |  |  |  | 230 | 230 | 230 | V | 230 | 230 | 230 | V
Load current |  |  |  |  | 18.7 | 28.1 | 18.8 | A | 19.8 | 29.5 | 18.6 | A
Load active power |  |  |  |  | 1.9 | 6.4 | 3.9 | kW | 4.3 | 6.5 | 4.1 | kW
Load reactive power |  |  |  |  | -1.5 | -1.4 | -1.3 | kVar | -1.8 | -1.9 | -1.3 | kVar
Load apparent power |  |  |  |  | 4.4 | 6.4 | 4.1 | kVA | 4.5 | 6.8 | 4.5 | kVA
Load of nominal |  |  |  |  | 12 | 19 | 12 | % | 13 | 20 | 13 | %
Test & Control Checklist:
See separate page.
[5 empty] | °C | 20
[13 empty] | In use since: |  | Commissioning
[13 empty] | In use since: |  | Commissioning
[13 empty] | In use since: |  | Commissioning
Measurements:
Rectifier input: | [9 empty] | Load:
Phase L1-N: |  | 239 | V | - | A |  |  |  |  | Phase L1-N: |  | 230.1 | V | - | A
Phase L2-N: |  | 240 | V | - | A |  |  |  |  | Phase L2-N: |  | 229.8 | V | - | A
Phase L3-N: |  | 241 | V | - | A |  |  |  |  | Phase L3-N: |  | 229.6 | V | - | A
| COMPLETED BY (Company / Person): | [5 empty] | ABB AS - Svein Andersen
| DATE: | [5 empty] | 2020-05-11
Tested INVERTER - BYPASS
Verified fan function:
Customer logbook update
Tested with diesel-generator
Battery test:
Max. charge current verified
Event Log File check (download)
Visual inspection
Cleaning
UPS room temperature:
Operating modes test
Remote alarms and controls test
SNMP Adapter
Check paramater settings
Battery charger function verified
Batt. Test active:
Yes
No:
External bypass:
Yes
No
Yes
No
Modules ON-OFF-ON
Control AC caps.:
Control DC caps.:

## Battery Measurement 3
Battery Test Records
Customer: | Digiplex Fet (DFAS) |  |  | Frame serial Nr.: |  | 5U 0111 |  |  | Address: |  | Heiaveien
Date of service: | 2020-05-11 |  |  | Frame No. (Hir): |  | 3 (Slave) |  |  | Customer contact: |  | Dag Brækken
UPS ID (Trinn/Side): | A1-2A UPS3 | [7 empty] | Contract Nr: |  | ABBUPS001115
String Values during Battery test: |  | MONITORED BY CELLWATCH
Mod: | S/N_ Branch For: |  | No Load V: | Load Applied.(W) |  | 1` Value (V) | 3` Value (V) | 7` Value (V) | 10` Value (V) | 20` Value (V) |  | 30` Value (V)
P 11: | DXM000424 |  | - | 15000 |  | 509 | 488 | 489 | 488 | 482 |  | 472
P 12: | DXM000420 |  | - | 15000 |  | 507 | 488 | 489 | 489 | 486 |  | 482
P 13: | DXM000415 |  | - | 15000 |  | 510 | 488 | 490 | 488 | 484 |  | 480
P 14: | DXM000421 |  | - | 15000 |  | 510 | 490 | 492 | 490 | 486 |  | 480
P 15: | DXM000423 |  | - | 15000 |  | 510 | 488 | 489 | 489 | 485 |  | 481
Test & Control Checklist:
[5 empty] | °C | 20
[5 empty] | Name: | -
REMARKS / CORRECTIONS: |  | Aut. Battery test performed 30min - Result: 1 x defec battery block found:
String P11 / Block 28 defect, voltage drop (10Vdc)
Room Conditions
Thermography
Termination and identification
DC Protection functionallity and Alarm

## System History
|  | Customer contact: |  | Dag Brækken
History Overview DPA 500 Site |  | A1-2A UPS1
Date | Ereignis: | Bemerkung: | Defektes Material | Störmelde- | Hardware | Software Version |  | Techniker
|  |  |  | Code | Version | EPROM | GAL