## IBS DPA 500 Master
ID-CARD DPA 500
FRAME 500 kVA
Customer: |  | Digiplex Fet (DFAS) | [5 empty] | Address: |  |  | Heiaveien
Date of service: |  | 26.05.2020 | [5 empty] | Customer contact: |  |  | Dag Braekken
UPS ID (Trinn/Side): |  | A1-3B | UPS1 |  |  |  |  | Service contract nr: |  |  | ABBUPS001115
UPS system |  | Conceptpower DPA500 | [5 empty] | Active |  |  | System int. nr. |  | Comm. Date
Frame serial Nr.: |  | 5U0136 |  |  |  |  | P 01: | DXM000484 |  |  | 1 |  | 2015-02-20
Frame No. (Hir): |  | 1 (Master) |  |  |  |  | P 02: | DXM000483 |  |  | 2 |  | 2015-02-20
Commiss. Date: |  | 02-2015 / 11-2016 |  |  |  |  | P 03: | DXM000469 |  |  | 3 |  | 2016-11-21
UPS Segment: |  | Datacenter |  |  |  |  | P 04 | DXM001559 |  |  | 4 |  | 2016-11-21
[7 empty] | P 05: | DXM001517 |  |  | 5 |  | 2016-11-21
GENERAL:
BATTERY | Backup time / load |  |  | 4 min / 100 kW |  |  | SYSTEM |  | SYSTEM CONFIGUR. |  | Parallell
| Amount of blocks |  |  | 40 |  |  |  |  | NR. PARALL. FRAMES |  | 3
| Set float voltage |  |  | 545 |  |  |  |  | MODULE POWER |  | 100KVA
| Set cut off voltage |  |  | 402 |  |  |  |  | NOMINAL VOLTAGE |  | 400V
| Charge current limitation |  |  | Yes |  |  |  |  | FREQUENCY |  | 50Hz
| Fast charge |  |  | Auto |  |  |  |  | SYNCH. WINDOW |  | Yes
| Common / modular |  |  | Modular |  |  |  |  | OPER. MODE |  | Online
| Manufacturer |  |  | Marathon
| Type |  |  | XL12V70
| Nominal capcity |  |  | 66.6 Ah
SET-UP INFO | ACTIVE MODULE SERIAL NR |  |  |  | DXM000484 |  | DXM000483 |  | DXM000469 | DXM001559 |  | DXM001517
| DATE(MONTH) OF MANUFACT. |  |  |  | 02.2015 |  | 02.2015 |  | 02.2015 | 09.2016 |  | 09.2016
| EPROM VER |  |  |  | 1.55 448D |  | 1.55 448D |  | 1.55 448D | 1.8 94BE |  | 1.8 94BE
| HARDWARE VERSION |  |  |  | 080 |  | 080 |  | 80 | 180 |  | 180
| DYN. PASSWORD |  |  |  | NO |  | NO |  | NO | NO |  | NO
REMARKS | All fans and rear connections inspected and OK. Downloaded system event log
5 year service of Passive & Active Modules Maintenance : Fan and capacitor replacement performed 2020
Aut. Battery test performed 30min - Result: OK
ABB Service Engineers (On-Site): |  |  |  |  | 1. | Svein Erik Andersen
[5 empty] | 2. | Christopher Kooij
Customer Representative (On-Site): |  |  |  |  | 3. | Dag Braekken
Common battery
Modular battery
SNMP Standard
SNMP Modbus
General alarm when redundancy lost
General alarm when first alarm
Output breaker pos. connected
External bypass pos. connected
Single Feed Input
Dual Feed Input
Other external connection, specity in "remarks"
Internal maint. bypass
External maint. bypass

## REV DPA 500 Master
Revision DPA 500
FRAME 500 kVA
Kunde: |  |  | Digiplex Fet (DFAS) |  |  |  | Address: |  |  |  | Heiaveien
Date of service: |  |  | 26.05.2020 |  |  |  | Customer contact: |  |  |  | Dag Braekken
UPS ID (Trinn/Side): |  |  | A1-3B |  |  |  | Contract Nr: |  |  |  | ABBUPS001115
Frame No: |  |  | Frame 1 |  |  | Mod: |  | Active: |  |  |  | Passive:
Frame Serial Nr: |  |  | 5U0136 |  |  | P 01: |  | DXM000484 |  |  |  | 0
Frame Hir: |  |  | 1 (Master) |  |  | P 02: |  | DXM000483 |  |  |  | 0
[6 empty] | P 03: |  | DXM000469 |  |  |  | 0
[6 empty] | P 04: |  | DXM001559 |  |  |  | 0
[6 empty] | P 05: |  | DXM001517 |  |  |  | 0
System display readings: |  |  |  | P 01: | DXM000484 |  |  | P 02: | DXM000483 |  |  | P 03: | DXM000469
Battery float voltage |  |  |  | 545 |  |  |  | 545 |  |  |  | 545
|  |  |  | L1 | L2 | L3 |  | L1 | L2 | L3 |  | L1 | L2 | L3
Rectifier voltage |  |  |  | 237 | 238 | 239 | V | 237 | 238 | 239 | V | 237 | 238 | 239 | V
Bypass voltage |  |  |  | 237 | 238 | 239 | V | 237 | 238 | 239 | V | 237 | 238 | 239 | V
Inverter output voltage |  |  |  | 230 | 230 | 230 | V | 230 | 230 | 230 | V | 230 | 230 | 230 | V
Load current |  |  |  | 9.6 | 9.5 | 7.5 | A | 9.1 | 7.4 | 7.3 | A | 10 | 7.2 | 7.7 | A
Load active power |  |  |  | 2 | 1.6 | 1.5 | kW | 2.1 | 1.6 | 1.6 | kW | 2 | 1.6 | 1.7 | kW
Load reactive power |  |  |  | -0.8 | -0.7 | -0.6 | kVar | -0.8 | -0.7 | -0.6 | kVar | -0.7 | -0.6 | -0.7 | kVar
Load apparent power |  |  |  | 2.1 | 1.8 | 1.7 | kVA | 2.2 | 1.8 | 1.6 | kVA | 2.2 | 1.7 | 1.8 | kVA
Load of nominal |  |  |  | 6 | 5 | 5 | % | 6 | 5 | 5 | % | 6 | 5 | 5 | %
|  |  |  | P 04 | DXM001559 |  |  | P 05: | DXM001517
Battery float voltage |  |  |  | 545 |  |  |  | 545
|  |  |  | L1 | L2 | L3 |  | L1 | L2 | L3
Rectifier voltage |  |  |  | 237 | 238 | 239 | V | 237 | 238 | 239 | V
Bypass voltage |  |  |  | 237 | 238 | 239 | V | 237 | 238 | 239 | V
Inverter output voltage |  |  |  | 230 | 230 | 230 | V | 230 | 230 | 230 | V
Load current |  |  |  | 8.3 | 7 | 7.6 | A | 8.5 | 6.4 | 7.3 | A
Load active power |  |  |  | 1.9 | 1.5 | 1.6 | kW | 2 | 1.4 | 1.5 | kW
Load reactive power |  |  |  | -0.4 | -0.3 | -0.2 | kVar | -0.2 | -0.3 | -0.3 | kVar
Load apparent power |  |  |  | 1.9 | 1.6 | 1.6 | kVA | 1.9 | 1.5 | 1.6 | kVA
Load of nominal |  |  |  | 5 | 5 | 5 | % | 5 | 4 | 4 | %
Test & Control Checklist:
See separate page.
|  |  |  | °C | 20
[12 empty] | In use since: |  | Comm/Sample
[12 empty] | In use since: |  | Comm/Sample
[12 empty] | In use since: |  | Comm/Sample
Measurements:
Rectifier input: | [8 empty] | Load:
Phase L1-N: |  | 237 | V | [5 empty] | Phase L1-N: |  | 230 | V
Phase L2-N: |  | 238 | V | [5 empty] | Phase L2-N: |  | 230 | V
Phase L3-N: |  | 238 | V | [5 empty] | Phase L3-N: |  | 230 | V
| COMPLETED BY (Company / Person): |  |  |  |  | Svein Erik Andersen
| DATE: |  |  |  |  | 2020-05-26
Tested INVERTER - BYPASS
Verified fan function:
Customer logbook update
Tested with diesel-generator
Battery test:
Max. charge current verified
Event Log File check (download)
Visual inspection
Cleaning
UPS room temperature:
Operating modes test
Remote alarms and controls test
SNMP Adapter
Check paramater settings
Battery charger function verified
Batt. Test active:
Yes
No:
External bypass:
Yes
No
Yes
No
Modules ON-OFF-ON
Control AC caps.:
Control DC caps.:

## Battery Measurement 1
Battery Test Records
Customer: | Digiplex Fet (DFAS) |  |  | Frame serial Nr.: |  | 5U0136 |  |  | Address: |  | Heiaveien
Date of service: | 26.05.2020 |  |  | Frame No. (Hir): |  | 1 (Master) |  |  | Customer contact: |  | Dag Braekken
UPS ID (Trinn/Side): | A1-3B | [7 empty] | Contract Nr: |  | ABBUPS001115
String Values during Battery test:
Mod: | S/N_ Branch For: |  | No Load V: | Load Applied.(W) |  | 1` Value (V) | 3` Value (V) | 7` Value (V) | 10` Value (V) | 20` Value (V) |  | 30` Value (V)
P 01: | DXM000484 |  | 545 | 4000 |  | 533 | 485 | 492 | 492 | 492 |  | 492
P 02: | DXM000483 |  | 545 | 4000 |  | 530 | 486 | 493 | 494 | 494 |  | 493
P 03: | DXM000469 |  | 545 | 4000 |  | 534 | 485 | 490 | 491 | 491 |  | 490
P 04: | DXM001559 |  | 545 | 4000 |  | 534 | 486 | 494 | 494 | 494 |  | 494
P 05: | DXM001517 |  | 545 | 4000 |  | 534 | 485 | 492 | 493 | 493 |  | 492
Test & Control Checklist:
[5 empty] | °C | 20
[5 empty] | Name: | Check
REMARKS / CORRECTIONS: |  | Aut. Battery test performed 30min - Result: OK
Room Conditions
Thermography
Termination and identification
DC Protection functionallity and Alarm

## IBS DPA 500 Middle
ID-CARD DPA 500
FRAME 500 kVA
Customer: |  | Digiplex Fet (DFAS) | [5 empty] | Address: |  |  | Heiaveien
Date of service: |  | 26.05.2020 | [5 empty] | Customer contact: |  |  | Dag Braekken
UPS ID (Trinn/Side): |  | A1-3B | UPS2 |  |  |  |  | Service contract nr: |  |  | ABBUPS001115
UPS system |  | Conceptpower DPA500 | [5 empty] | Active |  |  | System int. nr. |  | Comm. Date
Frame serial Nr.: |  | 5U 0138 |  |  |  |  | P 06: | DXM000487 |  |  | 1 |  | 2015-02-20
Frame No. (Hir): |  | 2 (Slave) |  |  |  |  | P 07: | DXM000462 |  |  | 2 |  | 2015-02-20
Commiss. Date: |  | 02-2015 / 11-2016 |  |  |  |  | P 08: | DXM000482 |  |  | 3 |  | 2016-11-21
UPS Segment: |  | Datacenter |  |  |  |  | P 09: | DXM000464 |  |  | 4 |  | 2016-11-21
[7 empty] | P 10: | DXM001495 |  |  | 5 |  | 2016-11-21
GENERAL:
BATTERY | Backup time / load |  |  | 4 min / 100 kW |  |  | SYSTEM |  | SYSTEM CONFIGUR. |  | Parallell
| Amount of blocks |  |  | 40 |  |  |  |  | NR. PARALL. FRAMES |  | 3
| Set float voltage |  |  | 545 |  |  |  |  | MODULE POWER |  | 100KVA
| Set cut off voltage |  |  | 402 |  |  |  |  | NOMINAL VOLTAGE |  | 400V
| Charge current limitation |  |  | Yes |  |  |  |  | FREQUENCY |  | 50Hz
| Fast charge |  |  | Auto |  |  |  |  | SYNCH. WINDOW |  | Yes
| Common / modular |  |  | Modular |  |  |  |  | OPER. MODE |  | Online
| Manufacturer |  |  | Marathon
| Type |  |  | XL12V70
| Nominal capcity |  |  | 66.6 Ah
SET-UP INFO | ACTIVE MODULE SERIAL NR |  |  |  | DXM000487 |  | DXM000462 |  | DXM000482 | DXM000464 |  | DXM001495
| DATE(MONTH) OF MANUFACT. |  |  |  | 02.2015 |  | 02.2015 |  | 02.2015 | 02.2015 |  | 09.2016
| EPROM VER |  |  |  | 1.55 448D |  | 1.55 448D |  | 1.55 448D | 1.55 448D |  | 1.8 94BE
| HARDWARE VERSION |  |  |  | 080 |  | 080 |  | 080 | 080 |  | 180
| DYN. PASSWORD |  |  |  | NO |  | NO |  | NO | NO |  | NO
REMARKS | All fans and rear connections inspected and OK. Downloaded system event log
5 year service of Passive & Active Modules Maintenance : Fan and capacitor replacement performed 2020
Aut. Battery test performed 30min - Result: OK
ABB Service Engineers (On-Site): |  |  |  |  | 1. | Svein Erik Andersen
[5 empty] | 2. | Christopher Kooij
Customer Representative (On-Site): |  |  |  |  | 3. | Dag Braekken
Common battery
Modular battery
SNMP Standard
SNMP Modbus
General alarm when redundancy lost
General alarm when first alarm
Output breaker pos. connected
External bypass pos. connected
Single Feed Input
Dual Feed Input
Other external connection, specity in "remarks"
Internal maint. bypass
External maint. bypass

## REV DPA 500 Middle
Revision DPA 500
FRAME 500 kVA
Kunde: |  |  | Digiplex Fet (DFAS) |  |  |  | Address: |  |  |  | Heiaveien
Date of service: |  |  | 26.05.2020 |  |  |  | Customer contact: |  |  |  | Dag Braekken
UPS ID (Trinn/Side): |  |  | A1-3B |  |  |  | Contract Nr: |  |  |  | ABBUPS001115
Frame No: |  |  | Frame 2 |  |  | Mod: |  | Active: |  |  |  | Passive:
Frame Serial Nr: |  |  | 5U 0138 |  |  | P 06: |  | DXM000487 |  |  |  | 0
Frame Hir: |  |  | 2 (Slave) |  |  | P 07: |  | DXM000462 |  |  |  | 0
[6 empty] | P 08: |  | DXM000482 |  |  |  | 0
[6 empty] | P 09: |  | DXM000464 |  |  |  | 0
[6 empty] | P 10: |  | DXM001495 |  |  |  | 0
System display readings: |  |  |  | P 06: | DXM000487 |  |  | P 07: | DXM000462 |  |  | P 08: | DXM000482
Battery float voltage |  |  |  | 545 |  |  |  | 545 |  |  |  | 545
|  |  |  | L1 | L2 | L3 |  | L1 | L2 | L3 |  | L1 | L2 | L3
Rectifier voltage |  |  |  | 237 | 238 | 239 | V | 237 | 238 | 239 | V | 237 | 238 | 239 | V
Bypass voltage |  |  |  | 237 | 238 | 239 | V | 237 | 238 | 239 | V | 237 | 238 | 239 | V
Inverter output voltage |  |  |  | 230 | 230 | 230 | V | 230 | 230 | 230 | V | 230 | 230 | 230 | V
Load current |  |  |  | 9.1 | 8 | 7.8 | A | 9.2 | 7.7 | 7.5 | A | 10.1 | 7 | 7.9 | A
Load active power |  |  |  | 2 | 1.7 | 1.5 | kW | 2 | 1.5 | 1.6 | kW | 2.1 | 1.5 | 1.5 | kW
Load reactive power |  |  |  | -0.8 | -0.8 | -0.8 | kVar | -0.5 | -0.7 | -0.7 | kVar | -0.8 | -0.7 | -0.6 | kVar
Load apparent power |  |  |  | 2.3 | 1.8 | 1.8 | kVA | 2.1 | 1.7 | 1.8 | kVA | 2.2 | 1.7 | 1.8 | kVA
Load of nominal |  |  |  | 6 | 5 | 5 | % | 6 | 5 | 5 | % | 6 | 5 | 5 | %
|  |  |  | P 09: | DXM000464 |  |  | P 10: | DXM001495
Battery float voltage |  |  |  | 545 |  |  |  | 545
|  |  |  | L1 | L2 | L3 |  | L1 | L2 | L3
Rectifier voltage |  |  |  | 237 | 238 | 239 | V | 237 | 238 | 239 | V
Bypass voltage |  |  |  | 237 | 238 | 239 | V | 237 | 238 | 239 | V
Inverter output voltage |  |  |  | 230 | 230 | 230 | V | 230 | 230 | 230 | V
Load current |  |  |  | 9.7 | 7.4 | 7.5 | A | 8.2 | 6.3 | 6.4 | A
Load active power |  |  |  | 2.1 | 1.6 | 1.8 | kW | 1.9 | 1.4 | 1.4 | kW
Load reactive power |  |  |  | -0.8 | -0.8 | -0.6 | kVar | -0.3 | -0.1 | -0.2 | kVar
Load apparent power |  |  |  | 2.2 | 1.9 | 1.9 | kVA | 1.9 | 1.4 | 1.5 | kVA
Load of nominal |  |  |  | 6 | 5 | 5 | % | 5 | 4 | 4 | %
Test & Control Checklist:
See separate page.
|  |  |  | °C | 20
[12 empty] | In use since: |  | Commissioning
[12 empty] | In use since: |  | Commissioning
[12 empty] | In use since: |  | Commissioning
Measurements:
Rectifier input: | [8 empty] | Load:
Phase L1-N: |  | 237 | V | [5 empty] | Phase L1-N: |  | 230 | V
Phase L2-N: |  | 238 | V | [5 empty] | Phase L2-N: |  | 230 | V
Phase L3-N: |  | 238 | V | [5 empty] | Phase L3-N: |  | 230 | V
| COMPLETED BY (Company / Person): |  |  |  |  | Svein E. Andersen/ABB
| DATE: |  |  |  |  | 2020-05-26
Tested INVERTER - BYPASS
Verified fan function:
Customer logbook update
Tested with diesel-generator
Battery test:
Max. charge current verified
Event Log File check (download)
Visual inspection
Cleaning
UPS room temperature:
Operating modes test
Remote alarms and controls test
SNMP Adapter
Check paramater settings
Battery charger function verified
Batt. Test active:
Yes
No:
External bypass:
Yes
No
Yes
No
Modules ON-OFF-ON
Control AC caps.:
Control DC caps.:

## Battery Measurement 2
Battery Test Records
Customer: | Digiplex Fet (DFAS) |  |  | Frame serial Nr.: |  | 5U 0138 |  |  | Address: |  | Heiaveien
Date of service: | 26.05.2020 |  |  | Frame No. (Hir): |  | 2 (Slave) |  |  | Customer contact: |  | Dag Braekken
UPS ID (Trinn/Side): | A1-3B | [7 empty] | Contract Nr: |  | ABBUPS001115
String Values during Battery test:
Mod: | S/N_ Branch For: |  | No Load V: | Load Applied.(W) |  | 1` Value (V) | 3` Value (V) | 7` Value (V) | 10` Value (V) | 20` Value (V) |  | 30` Value (V)
P 06: | DXM000487 |  | 545 | 4000 |  | 530 | 483 | 489 | 489 | 489 |  | 488
P 07: | DXM000462 |  | 545 | 4000 |  | 531 | 485 | 491 | 491 | 491 |  | 490
P 08: | DXM000482 |  | 545 | 4000 |  | 532 | 485 | 492 | 492 | 492 |  | 492
P 09: | DXM000464 |  | 545 | 4000 |  | 531 | 482 | 488 | 488 | 488 |  | 488
P 10: | DXM001495 |  | 545 | 4000 |  | 531 | 485 | 492 | 492 | 492 |  | 492
Test & Control Checklist:
[5 empty] | °C | 20
[5 empty] | Name: | Check
REMARKS / CORRECTIONS: |  | Aut. Battery test performed 30min - Result: OK
Room Conditions
Thermography
Termination and identification
DC Protection functionallity and Alarm

## IBS DPA 500 End Frame
ID-CARD DPA 500
FRAME 500 kVA
Customer: |  | Digiplex Fet (DFAS) | [5 empty] | Address: |  |  | Heiaveien
Date of service: |  | 26.05.2020 | [5 empty] | Customer contact: |  |  | Dag Braekken
UPS ID (Trinn/Side): |  | A1-3B | UPS3 |  |  |  |  | Service contract nr: |  |  | ABBUPS001115
UPS system |  | Conceptpower DPA500 | [5 empty] | Active |  |  | System int. nr. |  | Comm. Date
Frame serial Nr.: |  | 5U 0135 |  |  |  |  | P 11: | DXM000480 |  |  | 1 |  | 2015-02-20
Frame No. (Hir): |  | 3 (Slave) |  |  |  |  | P 12: | DXM000481 |  |  | 2 |  | 2015-02-20
Commiss. Date: |  | 02-2015 / 11-2016 |  |  |  |  | P 13: | DXM000567 |  |  | 3 |  | 2016-11-21
UPS Segment: |  | Datacenter |  |  |  |  | P 14: | DXM000471 |  |  | 4 |  | 2016-11-21
[7 empty] | P 15: | DXM000460 |  |  | 5 |  | 2016-11-21
GENERAL:
BATTERY | Backup time / load |  |  | 4 min / 100 kW |  |  | SYSTEM |  | SYSTEM CONFIGUR. |  | parallell
| Amount of blocks |  |  | 40 |  |  |  |  | NR. PARALL. FRAMES |  | 3
| Set float voltage |  |  | 545 |  |  |  |  | MODULE POWER |  | 100
| Set cut off voltage |  |  | 402 |  |  |  |  | NOMINAL VOLTAGE |  | 400V
| Charge current limitation |  |  | Yes |  |  |  |  | FREQUENCY |  | 50Hz
| Fast charge |  |  | Auto |  |  |  |  | SYNCH. WINDOW |  | Yes
| Common / modular |  |  | Modular |  |  |  |  | OPER. MODE |  | Online
| Manufacturer |  |  | Marathon
| Type |  |  | XL12V70
| Nominal capcity |  |  | 66.6 Ah
SET-UP INFO | ACTIVE MODULE SERIAL NR |  |  |  | DXM000480 |  | DXM000481 |  | DXM000567 | DXM000471 |  | DXM000460
| DATE(MONTH) OF MANUFACT. |  |  |  | 02.2015 |  | 02.2015 |  | 05.2014 | 06.2015 |  | 02.2015
| EPROM VER |  |  |  | 1.55 448D |  | 1.55 448D |  | 1.4 AB5B | 1.55 448D |  | 1.55 448D
| HARDWARE VERSION |  |  |  | 080 |  | 080 |  | 080 | 080 |  | 080
| DYN. PASSWORD |  |  |  | NO |  | NO |  | NO | NO |  | NO
REMARKS | All fans and rear connections inspected and OK. Downloaded system event log
5 year service of Passive & Active Modules Maintenance : Fan and capacitor replacement performed 2020
Aut. Battery test performed 30min - Result: OK
ABB Service Engineers (On-Site): |  |  |  |  | 1. | Svein Erik Andersen
[5 empty] | 2. | Christopher Kooij
Customer Representative (On-Site): |  |  |  |  | 3. | Dag Braekken
Common battery
Modular battery
SNMP Standard
SNMP Modbus
General alarm when redundancy lost
General alarm when first alarm
Output breaker pos. connected
External bypass pos. connected
Single Feed Input
Dual Feed Input
Other external connection, specity in "remarks"
Internal maint. bypass
External maint. bypass

## REV DPA 500 End Frame
Revision DPA 500
FRAME 500 kVA
Kunde: |  |  | Digiplex Fet (DFAS) |  |  |  | Address: |  |  |  | Heiaveien
Date of service: |  |  | 26.05.2020 |  |  |  | Customer contact: |  |  |  | Dag Braekken
UPS ID (Trinn/Side): |  |  | A1-3B |  |  |  | Contract Nr: |  |  |  | ABBUPS001115
Frame No: |  |  | Frame 3 |  |  | Mod: |  | Active: |  |  |  | Passive:
Frame Serial Nr: |  |  | 5U 0135 |  |  | P 11: |  | DXM000480 |  |  |  | 0
Frame Hir: |  |  | 3 (Slave) |  |  | P 12: |  | DXM000481 |  |  |  | 0
[6 empty] | P 13: |  | DXM000567 |  |  |  | 0
[6 empty] | P 14: |  | DXM000471 |  |  |  | 0
[6 empty] | P 15: |  | DXM000460 |  |  |  | 0
System display readings: |  |  |  | P 11: | DXM000480 |  |  | P 12: | DXM000481 |  |  | P 13: | DXM000567
Battery float voltage |  |  |  | 545 |  |  |  | 545 |  |  |  | 545
|  |  |  | L1 | L2 | L3 |  | L1 | L2 | L3 |  | L1 | L2 | L3
Rectifier voltage |  |  |  | 237 | 238 | 239 | V | 237 | 238 | 239 | V | 237 | 238 | 239 | V
Bypass voltage |  |  |  | 237 | 238 | 239 | V | 237 | 238 | 239 | V | 237 | 238 | 239 | V
Inverter output voltage |  |  |  | 230 | 230 | 230 | V | 230 | 230 | 230 | V | 230 | 230 | 230 | V
Load current |  |  |  | 10 | 7.6 | 8 | A | 10 | 6.8 | 6.8 | A | 10 | 7.2 | 7.6 | A
Load active power |  |  |  | 2.1 | 1.5 | 1.7 | kW | 2 | 1.5 | 1.6 | kW | 2.1 | 1.5 | 1.5 | kW
Load reactive power |  |  |  | -0.9 | -0.7 | -0.6 | kVar | -0.6 | -0.4 | -0.4 | kVar | -0.7 | -0.7 | -0.7 | kVar
Load apparent power |  |  |  | 2.3 | 1.8 | 1.7 | kVA | 2.2 | 1.7 | 1.7 | kVA | 2.2 | 1.7 | 1.7 | kVA
Load of nominal |  |  |  | 7 | 5 | 5 | % | 6 | 5 | 5 | % | 6 | 5 | 5 | %
|  |  |  | P 14: | DXM000471 |  |  | P 15: | DXM000460
Battery float voltage |  |  |  | 545 |  |  |  | 545
|  |  |  | L1 | L2 | L3 |  | L1 | L2 | L3
Rectifier voltage |  |  |  | 237 | 238 | 239 | V | 237 | 238 | 239 | V
Bypass voltage |  |  |  | 237 | 238 | 239 | V | 237 | 238 | 239 | V
Inverter output voltage |  |  |  | 230 | 230 | 230 | V | 230 | 230 | 230 | V
Load current |  |  |  | 9.5 | 7.9 | 8.2 | A | 10 | 7.3 | 7.5 | A
Load active power |  |  |  | 2.1 | 1.6 | 1.7 | kW | 2.1 | 1.5 | 1.6 | kW
Load reactive power |  |  |  | -0.9 | -0.8 | -0.6 | kVar | -0.8 | -0.7 | -0.6 | kVar
Load apparent power |  |  |  | 2.2 | 1.7 | 1.8 | kVA | 2.2 | 1.6 | 1.7 | kVA
Load of nominal |  |  |  | 6 | 5 | 5 | % | 6 | 5 | 5 | %
Test & Control Checklist:
See separate page.
|  |  |  | °C | 20
[12 empty] | In use since: |  | Commissioning
[12 empty] | In use since: |  | Commissioning
[12 empty] | In use since: |  | Commissioning
Measurements:
Rectifier input: | [8 empty] | Load:
Phase L1-N: |  | 237 | V | [5 empty] | Phase L1-N: |  | 230 | V
Phase L2-N: |  | 238 | V | [5 empty] | Phase L2-N: |  | 230 | V
Phase L3-N: |  | 238 | V | [5 empty] | Phase L3-N: |  | 230 | V
| COMPLETED BY (Company / Person): |  |  |  |  | Svein E. Andersen/ABB
| DATE: |  |  |  |  | 2020-05-26
Tested INVERTER - BYPASS
Verified fan function:
Customer logbook update
Tested with diesel-generator
Battery test:
Max. charge current verified
Event Log File check (download)
Visual inspection
Cleaning
UPS room temperature:
Operating modes test
Remote alarms and controls test
SNMP Adapter
Check paramater settings
Battery charger function verified
Batt. Test active:
Yes
No:
External bypass:
Yes
No
Yes
No
Modules ON-OFF-ON
Control AC caps.:
Control DC caps.:

## Battery Measurement 3
Battery Test Records
Customer: | Digiplex Fet (DFAS) |  |  | Frame serial Nr.: |  | 5U 0135 |  |  | Address: |  | Heiaveien
Date of service: | 26.05.2020 |  |  | Frame No. (Hir): |  | 3 (Slave) |  |  | Customer contact: |  | Dag Braekken
UPS ID (Trinn/Side): | A1-3B | [7 empty] | Contract Nr: |  | ABBUPS001115
String Values during Battery test:
Mod: | S/N_ Branch For: |  | No Load V: | Load Applied.(W) |  | 1` Value (V) | 3` Value (V) | 7` Value (V) | 10` Value (V) | 20` Value (V) |  | 30` Value (V)
P 11: | DXM000480 |  | 545 | 4000 |  | 530 | 488 | 494 | 495 | 495 |  | 495
P 12: | DXM000481 |  | 545 | 4000 |  | 530 | 488 | 495 | 495 | 495 |  | 495
P 13: | DXM000567 |  | 545 | 4000 |  | 530 | 486 | 492 | 492 | 492 |  | 491
P 14: | DXM000471 |  | 545 | 4000 |  | 532 | 485 | 492 | 493 | 493 |  | 492
P 15: | DXM000460 |  | 545 | 4000 |  | 532 | 483 | 490 | 490 | 490 |  | 490
Test & Control Checklist:
[5 empty] | °C | 20
[5 empty] | Name: | Check
REMARKS / CORRECTIONS: |  | Aut. Battery test performed 30min - Result: OK
Room Conditions
Thermography
Termination and identification
DC Protection functionallity and Alarm

## System History
|  | Customer contact: |  | Dag Braekken
History Overview DPA 500 Site |  | A1-3B
Date | Ereignis: | Comment: | Defektes Material | Fault codes | Hardware | Software Version |  | Techniker
|  |  |  | Code | Version | EPROM | GAL

## Compatibility Report
Compatibility Report for PM A1-3 A-side_Service Protocol DFAS 18.06 2018.xls
Run on 13.06.2018 08:52
The following features in this workbook are not supported by earlier versions of Excel. These features may be lost or degraded when opening this workbook in an earlier version of Excel or if you save this workbook in an earlier file format.
Minor loss of fidelity | # of occurrences | Version
Some cells or styles in this workbook contain formatting that is not supported by the selected file format. These formats will be converted to the closest format available. | 68 | Excel 97-2003

## Compatibility Report (1)
Compatibility Report for PM A1-3 A-side_Service Protocol DFAS 18.06.2018.xls
Run on 13.06.2018 09:40
The following features in this workbook are not supported by earlier versions of Excel. These features may be lost or degraded when opening this workbook in an earlier version of Excel or if you save this workbook in an earlier file format.
Minor loss of fidelity | # of occurrences | Version
Some cells or styles in this workbook contain formatting that is not supported by the selected file format. These formats will be converted to the closest format available. | 68 | Excel 97-2003

## Compatibility Report (2)
Compatibility Report for PM A1-3 A-side_Service Protocol DFAS 18.06.2018.xls
Run on 13.06.2018 09:58
The following features in this workbook are not supported by earlier versions of Excel. These features may be lost or degraded when opening this workbook in an earlier version of Excel or if you save this workbook in an earlier file format.
Minor loss of fidelity | # of occurrences | Version
Some cells or styles in this workbook contain formatting that is not supported by the selected file format. These formats will be converted to the closest format available. | 68 | Excel 97-2003

## Compatibility Report (3)
Compatibility Report for PM A1-3 A-side_Service Protocol DFAS 18.06.2018.xls
Run on 13.06.2018 10:10
The following features in this workbook are not supported by earlier versions of Excel. These features may be lost or degraded when opening this workbook in an earlier version of Excel or if you save this workbook in an earlier file format.
Minor loss of fidelity | # of occurrences | Version
Some cells or styles in this workbook contain formatting that is not supported by the selected file format. These formats will be converted to the closest format available. | 68 | Excel 97-2003

## Compatibility Report (4)
Compatibility Report for PM A1-3 A-side_Service Protocol DFAS 18.06.2018.xls
Run on 13.06.2018 10:18
The following features in this workbook are not supported by earlier versions of Excel. These features may be lost or degraded when opening this workbook in an earlier version of Excel or if you save this workbook in an earlier file format.
Minor loss of fidelity | # of occurrences | Version
Some cells or styles in this workbook contain formatting that is not supported by the selected file format. These formats will be converted to the closest format available. | 68 | Excel 97-2003

## Compatibility Report (5)
Compatibility Report for PM A1-3 A-side_Service Protocol DFAS 18.06.2018.xls
Run on 13.06.2018 10:24
The following features in this workbook are not supported by earlier versions of Excel. These features may be lost or degraded when opening this workbook in an earlier version of Excel or if you save this workbook in an earlier file format.
Minor loss of fidelity | # of occurrences | Version
Some cells or styles in this workbook contain formatting that is not supported by the selected file format. These formats will be converted to the closest format available. | 68 | Excel 97-2003

## Compatibility Report (6)
Compatibility Report for PM A1-3 A-side_Service Protocol DFAS 18.06.2018.xls
Run on 13.06.2018 10:29
The following features in this workbook are not supported by earlier versions of Excel. These features may be lost or degraded when opening this workbook in an earlier version of Excel or if you save this workbook in an earlier file format.
Minor loss of fidelity | # of occurrences | Version
Some cells or styles in this workbook contain formatting that is not supported by the selected file format. These formats will be converted to the closest format available. | 68 | Excel 97-2003

## Compatibility Report (7)
Compatibility Report for PM A1-3 A-side_Service Protocol DFAS 18.06.2018.xls
Run on 13.06.2018 10:34
The following features in this workbook are not supported by earlier versions of Excel. These features may be lost or degraded when opening this workbook in an earlier version of Excel or if you save this workbook in an earlier file format.
Minor loss of fidelity | # of occurrences | Version
Some cells or styles in this workbook contain formatting that is not supported by the selected file format. These formats will be converted to the closest format available. | 68 | Excel 97-2003

## Compatibility Report (8)
Compatibility Report for PM A1-3 A-side_Service Protocol DFAS 18.06.2018.xls
Run on 14.06.2018 10:38
The following features in this workbook are not supported by earlier versions of Excel. These features may be lost or degraded when opening this workbook in an earlier version of Excel or if you save this workbook in an earlier file format.
Minor loss of fidelity | # of occurrences | Version
Some cells or styles in this workbook contain formatting that is not supported by the selected file format. These formats will be converted to the closest format available. | 68 | Excel 97-2003