## IEC Major Maintenance Report
Report Issue Number: | 1
Report Issued Date: | 2021-10-01
Project Number: | P121661
Project Name: | DigiPlex - DHAS-C (OSL21)
Unit Name: | C1 - DH1 - IEC 07
Project Information
Project Number: | P121661 |  |  | Project Name: |  | DigiPlex - DHAS-C (OSL21)
Client Reference: | OSL21
Site Information
Site Name: | DigiPlex - DHAS-C (OSL21)
Address: | Holtskogen 31
Town/City: | Tomter |  |  | Postcode: |  | 1825
Contact Name: | Geir Vistung |  |  | Contact Number: |  | +47 901 20 403
Equipment Information
Unit Name: | C1 - DH1 - IEC 07
Unit Serial Number: | 650196.0240 |  |  | Unit Model: |  | Adia-DENCO
Unit Airstreams: | Supply/Extract |  |  | Unit Installation: |  | Internal Unit (External Environment)
Unit Handing: | Right
Controller Information
Controller Type: | SAIA M90 |  |  | Software Version: |  |  | v1.2.3
Test Meters
Meter Name | Meter used for |  |  | Meter Serial Number |  | Meter Calibration Number |  | Meter Calibration Date | Meter Calibration Expiry Date
Testo 510i | Pressure |  |  | 49105036 |  | B00423/60881 |  | 2021-08-16 | 2022-08-16
Testo 510i | Pressure |  |  | 49141992 |  | B00423/60882 |  | 2021-08-16 | 2022-08-16
Testo 605i | Humidity/Temp |  |  | 83115240 |  | 524021 |  | 2021-08-06 | 2022-08-06
Testo 905i | Temp |  |  | 49517442 |  | 744221 |  | 2021-08-06 | 2022-08-06
Fluke 279FC | Voltage |  |  | 35900067 |  | 21-584171 |  | 2021-09-21 | 2022-09-21
Fluke 347FC | Ampere/Voltage |  |  | 36440266WS |  | 21-584168 |  | 2021-09-21 | 2022-09-21
Testo 510i | Pressure |  |  | 49141232 |  | B00423/60880 |  | 2021-08-16 | 2022-08-16
3. Overall Unit
Circle and number any areas (Left Hand Unit):
Service Side |  |  |  |  | Rear Side
Type (Damage, Seal or Corrosion) |  | Number |  | Comments
Circle and number any areas (Right Hand Unit):
Service Side |  |  |  |  | Rear Side
Type (Damage, Seal or Corrosion) |  | Number |  | Comments
Ok
All Door Stops fitted and operating correctly? |  |  |  | Yes
Alarm, Event & Maintenance Logs checked and OK? |  |  |  | Yes
Unit Cleaning (Hoovered/Wiped) carried out if required? |  |  |  | No
Notes:
4. Fans
Circle and number any areas:
Supply (Air Off Side) |  |  |  |  | Exhaust (Air Off Side)
Type (Debris, Damage or Corrosion) |  | Number |  | Comments
Ok
All fans checked and free from noise or vibration? |  |  |  |  | Yes
Fan & Fan Section Cleaning (Hoovered/Wiped) carried out if required? |  |  |  |  | No
Item for Calibration |  | Sensor Reading |  | Calibrated Reading |  | Offset Applied
Supply Fan Pressure Sensor |  | 265 |  | 263 |  | -2
Exhaust Fan Pressure Sensor |  | 366 |  | 365 |  | -1
Notes:
5. Filters
Circle and number any areas:
Fresh Air (Air On Side) |  |  |  |  | Return Air (Air On Side)
Type (Debris, Damage or Corrosion) |  | Number |  | Comments
Ok
Airstream | Actual Value (Pa) |  | Airflow (m3/h) |  | Fan Level (%) |  | Filter Dirty Limit
Fresh Air / Exhaust Air | 23 |  | 22284 |  | 50 |  | 150
Return Air / Supply Air | 17 |  | 30317 |  | 50 |  | 150
Filter Section Cleaning (Hoovered/Wiped) carried out if required? |  |  |  |  | Yes
Item for Calibration |  | Sensor Reading |  | Calibrated Reading |  | Offset Applied
Fresh Air Filter Pressure Sensor |  | 23 |  | 21 |  | -2
Return Air Filter Pressure Sensor |  | 17 |  | 22 |  | 5
Fresh Air Filters (Ambient Airstream) Replaced? |  |  |  | Yes
Return Air Filters (Data Centre Airstream) Replaced? |  |  |  | Yes
Notes:
1 x 287x287x360 filter missing on fresh air , not changed, and 4 fresh air filters are 287x592x360, but should be 592x287x360.
6. Exchangers (Coils & Plates)
Circle and number any areas:
Plate Exchanger |  |  |  |  | HR/Snow Melt Coil
Type (Debris, Damage or Corrosion) |  | Number |  | Comments
Ok
Checked for and free from any signs of leaks? |  |  |  |  | Yes
Exchanger Section(s) Cleaning (Hoovered/Wiped) carried out if required? |  |  |  |  | No
Notes:
7. Dampers
Winter By-Pass Damper driven end to end and physically witnessed? |  |  |  |  | Yes
Exhaust Air Damper driven end to end and physically witnessed? |  |  |  |  | Yes
Return Air Damper driven end to end and physically witnessed? |  |  |  |  | Yes
HR/Snow Melt By-Pass Damper driven end to end and physically witnessed? |  |  |  |  | Yes
Supply Air Damper driven end to end and physically witnessed? |  |  |  |  | Yes
Dampers & Damper Sections Cleaning (Hoovered/Wiped) carried out if required? |  |  |  |  | No
Notes:
8. Adiabatic Water System
Circle and number any areas (Left Hand Unit):
Type (Leak, Scale or Deposit/slurry) |  | Number |  | Comments
Circle and number any areas (Right Hand Unit):
Type (Leak, Scale or Deposit/slurry) |  | Number |  | Comments
Water is closed due low temp.
Water tank was full of pollen. Took time to
Clean it.
Adiabatic Pump Discharge Strainer Checked and if required cleaned? | [5 empty] | Yes
Adiabatic Tank Water Level Sensor Rod checked for Tightness (4 Nm)?: | [5 empty] | Yes
Adiabatic Spray Nozzles checked to ensure they give an even cone and if required cleaned? | [5 empty] | Yes
Adiabatic Sump Manual Drain Valve Checked for correct operation? | [5 empty] | NA
Item for Calibration |  | Sensor Reading |  | Calibrated Reading |  | Offset Applied
Adiabatic Tank Water Level Sensor |  | NA
Adiabatic Tank Water Temperature |  | NA
9. Controls & Control Panel
Overload settings checked and OK? |  |  |  | Yes
Main Controller checked for any battery warning messages and OK? |  |  |  | Yes
UPS Battery Condition checked and OK? |  |  |  | Yes
Plant Operating Hours: | 5791
Adiabatic Operating Hours: | 267
Total Water Consumption: | 98.762
Voltage Readings (Calibrated Readings)
L1 -> N: | 239 |  | L2 -> N: | 239 |  | L3 -> N: | 239
L1 -> L2: | 414 |  | L1 -> L3: | 414 |  | L2 -> L3: | 414
Current Readings (Calibrated Readings)
SUPPLY FAN
Fan Level: | 50
Fan 1 Current: | L1: | 1.1 |  | L2: | 1.1 |  | L3: | 1.1
Fan 2 Current: | L1: | 1.1 |  | L2: | 1.1 |  | L3: | 1.1
Fan 3 Current: | L1: | 1.1 |  | L2: | 1.1 |  | L3: | 1.1
Fan 4 Current: | L1: | 1.1 |  | L2: | 1.1 |  | L3: | 1.1
Fan 5 Current: | L1: | 1.1 |  | L2: | 1.1 |  | L3: | 1.1
Fan 6 Current: | L1: | 1.1 |  | L2: | 1 |  | L3: | 1
EXHAUST FAN
Fan Level: | 50
Fan 1 Current: | L1: | 0.8 |  | L2: | 0.8 |  | L3: | 0.8
Fan 2 Current: | L1: | 0.8 |  | L2: | 0.8 |  | L3: | 0.8
Fan 3 Current: | L1: | 0.8 |  | L2: | 0.8 |  | L3: | 0.8
Fan 4 Current: | L1: | 0.8 |  | L2: | 0.8 |  | L3: | 0.8
Control Panel Section Cleaning (Hoovered/Wiped) carried out if required? |  |  |  |  | Yes
Item for Calibration |  | Sensor Reading |  | Calibrated Reading |  | Offset Applied
Fresh Air Temperature Sensor |  | 10.9 |  | 11.1 |  | 0.2
Fresh Air Humidity Sensor |  | 94 |  | 91.5 |  | -2.5
Plate Air On Temperature Sensor |  | 11.6 |  | 10.5 |  | -1.1
Supply Air Temperature Sensor |  | 30 |  | 30.4 |  | 0.4
Duct/Whitespace Pressure Sensor |  | 51 |  | 50 |  | -1
Return Air Temperature Sensor |  | 33.3 |  | 35.1 |  | 1.8
Return Air Humidity Sensor |  | 25.6 |  | 30.4 |  | 4.8
Notes:
General
Maintenance Current Operating Hours Reset (Using the IEC Unit User Interface): |  |  |  |  | Yes
I confirm I have maintained the unit as per the maintenance task list:
Name: | Bjørnar Strandos / Alf Johansen |  |  |  | Date: | 2021-10-01
Position:
Signature